<<Facility Name>>

|  |  |  |  |  |  |  |  |  |  | Comments/Corrective Actions |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date of inspection |  |  |  |  |  |  |  |  |  |  |
| Inspection performed by |  |  |  |  |  |  |  |  |  |  |
| General condition of prime mover/generator |  |  |  |  |  |  |  |  |  |  |
| Condition of belts & hoses |  |  |  |  |  |  |  |  |  |  |
| Engine oil level |  |  |  |  |  |  |  |  |  |  |
| Lube oil heater |  |  |  |  |  |  |  |  |  |  |
| Coolant level |  |  |  |  |  |  |  |  |  |  |
| Water pump |  |  |  |  |  |  |  |  |  |  |
| Jacket water heater |  |  |  |  |  |  |  |  |  |  |
| Radiator |  |  |  |  |  |  |  |  |  |  |
| Electrical/Generator breaker closed |  |  |  |  |  |  |  |  |  |  |
| Battery system: |  |  |  |  |  |  |  |  |  |  |
| Electrolyte level |  |  |  |  |  |  |  |  |  |  |
| Charger |  |  |  |  |  |  |  |  |  |  |
| Exhaust system |  |  |  |  |  |  |  |  |  |  |
| Fuel system: |  |  |  |  |  |  |  |  |  |  |
| Fuel supply level |  |  |  |  |  |  |  |  |  |  |
| Tank vent(s) |  |  |  |  |  |  |  |  |  |  |

Emergency Generator – Weekly Inspection Checklist

ANY TOWN NURSING HOME

|  |  |  |  |  |  |  |  |  |  | Comments/Corrective Actions |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date of inspection | 9/18/08 | 9/25/08 | 10/2/08 |  |  |  |  |  |  |  |
| Inspection performed by | JJS | JJS | JJS |  |  |  |  |  |  |  |
| General condition of prime mover/generator | OK | OK | OK |  |  |  |  |  |  |  |
| Condition of belts & hoses | OK | OK | OK |  |  |  |  |  |  |  |
| Engine oil level | OK | OK | OK |  |  |  |  |  |  | Checked with engine stopped |
| Lube oil heater | OK | OK | OK |  |  |  |  |  |  |  |
| Coolant level | OK | OK | OK |  |  |  |  |  |  |  |
| Water pump | OK | OK | OK |  |  |  |  |  |  |  |
| Jacket water heater | OK | OK | OK |  |  |  |  |  |  |  |
| Radiator | OK | OK | OK1 |  |  |  |  |  |  | 1(10/2/08) Cores need cleaning - Done |
| Electrical/Generator breaker closed | OK | OK | OK |  |  |  |  |  |  |  |
| Battery system: | OK1 | OK | OK |  |  |  |  |  |  | 1(9/18/08) Topped off electrolyte |
| Electrolyte level | OK | OK | OK |  |  |  |  |  |  | Normal = 1250 |
| Charger | OK | OK | OK |  |  |  |  |  |  | Reads less than 1 amp |
| Exhaust system | OK | OK | OK |  |  |  |  |  |  |  |
| Fuel system: 2 | OK | OK | OK |  |  |  |  |  |  | 2(Natural Gas) |
| Fuel supply level | OK | OK1 | OK |  |  |  |  |  |  | 1(9/25/08) – ½ full, fuel added |
| Tank vent(s) | OK | OK | OK |  |  |  |  |  |  |  |

Emergency Generator – Weekly Inspection Checklist