## Chapter 3
Code Changes 2009 IEC to 2023 NEC |  |  |  | Draft for Review - July 15, 2024
2009 IEC |  | 2023 NEC |  | Fiscal | Summary
Paragraph | Description | Paragraph | Description | Impact | Change
300.2 (A) | Used for 600V nominal | 300.2 (A) | Used for 1000V AC nominal and 1500V DC nominal | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
300.3(B)(1) |  | 300.3(B)(1) | Added: "Connections, taps, or extensions made from paralleled conductors shall connect to all conductors of the paralleled set, grounded and ungrounded , as applicable." | None | Clarification
300.3 (C)(1) | Used for 600V nominal | 300.3 (C)(1) | Used for 1000V AC nominal and 1500V DC nominal | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
300.3 (C)(1) | Exception for solar photovoltaic | 300.3 (C)(1) | Exception removed | None | Requirements moved to Chapter 6.
300.3 (C)(2) | Over 600V | 300.3 (C)(2) | Changed to over 1000V AC nominal and 1500V DC nominal | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
300.3(D) | IEC - Separation from corrugated stainless steel tubing: All wiring methods shall be isolated from corrugated stainless steel tubing by a space separation of at least 2 inches except where the bonding connection is made. |  |  |  | 2009 IEC Amendment
300.4(A)(1) | References nearest edge to hole | 300.4(A)(1) | Removes "nearest" | Minimal | May require plating if bored hole falls within minimum of multiple edges.
300.4(A)(1) Exception 1 |  | 300.4(A)(1) Exception 1 | Added RTRC (fiberglass conduit) | Savings | Gives more options for conduit that does not need to be protected.
300.4(E) |  | 300.4(E) | Added: "A cable, raceway, or box shall not be installed in concealed locations in metal-corrugated, or sheet decking-type roof." | Cost | Restricts installations to RMC or IMC in concealed locations in metal roof corrugations' potentially requiring longer and/or more expensive pathways..
300.4(F) |  | 300.4(F) Exception 1 | Added PVC and RTRC (fiberglass conduit) |  | Gives more options for conduit that does not need to be protected.
|  | 300.4(H) | Added for clarification on requirement for expansion fittings. | None | Already required later in Chapter 3 under conduit requirements.
300.5(C) |  | 300.5(C) Exception 1 | Added exceptio0n to allow MI cable to be directly installed under a building without conduit. | Savings | Reduces cost for underground installations bellow buildings by allowing direct burial cable.
300.5(C) |  | 300.5(C) Exception 2 | Added exceptio0n to allow MC cable to be installed under a building without conduit if concrete encased. | Savings | Reduces cost for underground installations bellow buildings by allowing direct burial cable.
Table 300.5(A) |  | Table 300.5(A) | Allows MI cable to be directly installed under a building without conduit, or MC cable where concrete encased. | Savings | Reduces cost for underground installations bellow buildings by allowing direct burial cable.
300.5(D)(4) |  | 300.5(D)(4) | Added RTRC-XW | Savings | Gives more options for conduit that does not need to be protected.
300.5(G) |  | 300.5(G) | Clarified that requirement to seal underground conduits includes spare underground conduits | None | Clarification that requirement includes all conduits, including spares.
300.5(H)(1) Exception 1 |  | 300.5(H)(1) Exception 1 | Added 2nd paragraph detailing installation of direct-buried single conductors. | None | Clarification on intent
300.6 |  | 300.6 | Added require for corrosion protection to enclosures. | None | Clarification of requirements in subsequent articles of 300.6.
300.6(A) |  | 300.6(A) | Added require for corrosion protection to enclosures. | None | Clarification of requirements in subsequent articles of 300.6.
300.6(A) |  | 300.6(A) | Added requirement for applied corrosion protection on conduit threads where not threaded at the factory. | Cost | Stricter requirement for corrosion protection on Shop cut threading.
300.7(A) |  | 300.7(A) | Revised term "Cable raceway" to "raceway" | None | Wording to conform to definition of "raceway"
300.11(A) |  | 300.11(B) | Added (B) under section to amplify requirements above suspended ceilings. | None | Highlighting of requirements already under this section.
300.11(B) |  | 300.11(C) | Added Class3 cabling as system able to be supported from electrical raceway | Savings | Allows Class 3 wiring to be secured to raceway instead of having to be supported separately.
300.14 |  | 300.14 | Added clarification that 6-inch length in box may be spliced or unsliced. | None | Clarification.
300.15 |  | 300.15 | "Conductor transition point" added. | None | Clarification since transition requires a splice and would therefore already fall under this requirement.
300.15(M) | Box not required for closed-loop power distributi9on system for identified devices. | 300.15(M) | Removed. |  | Utility?
300.17 |  | 300.17 | Added "Cables" to requirements | None
300.18(A) |  | 300.18(A) | Added: "listed manufactured assemblies in accordance with 604.100" | Savings | Adds recognition of premanufactured assemblies which potentially be labor cost saving.
300.18(A) |  | 300.18(A) | Added "Cables" to requirements | None
300.22 |  | 3600.22 | Terminology updated to align with other NFPA documents and clarification of coverage of subsections following. | None | Intent and scope remain the same.
300.22(B) |  | 300.22(B) | Title clarifies applies to ducts specifically. | Savings | Narrows application and allows wiring methods within supply plenum ceilings.
300.22(B) |  | 300.22(B) Exception | Added exception for Plenum listed wiring to be used for connection specifically to devise within or associated with duct and less than 4-feet in length. | Savings | Allows for Plenum rated open cabling systems that will reduce material and labor costs.
300.22(C)(1) |  | 300.22(C)(1) | Added "non-metallic cable ties to secure and support cables allowed. | Savings | Allows for Plenum rated open cabling systems that will reduce material and labor costs.
300.22(C)(2) |  | 300.22(C)(2) | Added cable tray systems requirements for use in air handling spaces. | Savings | Allows for options for support of Plenum rated open cabling systems that will reduce material and labor costs.
|  | 300.25 | Added section to prohibit installation of electrical through exit enclosures and stair towers. | Cost | Will impact circuit routing.
|  | 300.26 | Added section partially defining Class 1, 2 and 3 and non-power limited circuits. | None | These definitions were already in the NEC. Added here for clarification?
300.31 |  | 305 | Changed requirements from over 600V to over 1000V, and 1500VDC and put under new section.
300.31 | Covers required | 305.7 | Location change. | None | Restructuring.
300.32 | Conductors of different systems - References 300.3(C)(2) | 305.4 | Similar, except 300.3(C)(2)(a) for secondary wiring to electric-discharge lamps drop, since this section applies to 1000V and over. | None | Restructuring.
300.34 | Conductor bending radius | 305.5 | Location change. | None | Restructuring.
300.35 | Protection against induction heating | 305.6 | Location change. | None | Restructuring.
300.37 | Above ground wiring methods | 305.3 | Revised descriptions to fit 1000V and over. Added references to RTRC and PVC. Added Table 305.3. | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
|  | 305.8 | Added section to clarify that interiors of above grade raceways in wet locations are considered wet. | Cost | May change conductor type.
300.39 | Braid-covered insulation conductors - exposed installation | 305.9 | Location change. | None | Restructuring.
300.40 | Insulation shielding | 305.10 | Location change. | None | Restructuring.
300.42 | Moisture or mechanical protection for metal-sheathed cables | 305.11 | Location change. | None | Restructuring.
|  | 305.11 | Added section requiring Danger Warning signs. | Cost | Cost of signage.
300.50 | Direct buried cables references 310.7 | 305.15(A) | Conductors for direct burial shall be of type identified for such use. | None | Referenced Section 310.7 had similar language on identified for use. Section 310.7 removed from 2023 NEC.
|  | 305.15(A)(2) | Added section on industrial applications allowing for unshielded single conductor installations. | Savings | Reduced costs for certain controlled industrial applications.
|  | 305.15(B) | Added section to clarify that interiors of underground raceways in wet locations are considered wet. | None | Conductor application for underground covered in section 310.
300.50(B) | Protection from damage | 305.15(C) | Added RTRC-XW raceway for riser pole applications. | Savings | Allows for lighter weight fiberglass conduit on poles.
|  | 305.4 | Replaces and reworded requirements previously under 300.3 (C)(2)(a) - (C)(2)(e)
310.1 | Conductors for general wiring - scope | 310.1 | Added covers conductors up to 2000V | None
310.2(A) | Insulated | 310.3(D) | Location change. | None | Restructuring.
310.2(B) | Conductor material | 310.3(B) | Location change. | None | Restructuring.
310.3 | Stranded conductors | 310.3(C) | Location change. | None | Restructuring.
310.4(A) | Conductors in parallel. Terms: "Phase, polarity, neutral or grounded circuit conductor" | 310.10(G) | Terms: "Circuit conductor, ungrounded conductor grounded conductor or neutral" | None | Change in terminology to follow updated standards.
310.5 | Minimum size of conductors illustrated with table | 310.3(A) | Simplified to Minimum size of conductors = 14 AWG CU or 12 AWG AL | ???
Table 310.4(1) |  | Table 310.4(1) | Added Moisture resistant thermoset (XHWN & XHWN-2) | None | Additional material options.
Table 310.4(1) |  | Table 310.4(1) | Added Note - Conductors in Table 310.4(1) permitted to be rated up to 1000V, if listed and marked | None | Additional material options.
Table 310.5 | Minimum size of conductors illustrated with table | Table 315.12(A) | Added smaller size for 5001V to 8000V | Savings | Possible use of smaller sized conductors
|  | 310.10(G)(6) | Added requirements for bonding jumpers. | None | Clarification of requirements already under Section 250.102.
310.6 | Shielding | 315.44 | Increased application up to 5000V for MC cables in industrial establishments. | Savings | Allows more flexibility for wiring methods up to 5000V.
310.6 | Shielding | 315.44 Exception 2 | Added for non-shielded insulated conductors listed up to 5000V to replace similar in supervised industrial establishments | Savings | Allows replacement in kind and does not require upgrade
310.7 | Direct -burial | 310.10(E) | Similar language on suitable for locations. | None
310.7 Exceptions | Direct -burial | 315.36 | Location change. | None | Restructuring.
310.8(A) | Locations - Dry locations | 310.10(A) | Location change. | None | Restructuring.
310.8(B) | Locations - Dry and damp locations | 310.10(B) | Location change. | None | Restructuring.
310.8(C) | Locations - Wet | 310.10(C) | Location change. | None | Restructuring.
310.8(D) | Locations - Exposed to direct sunlight | 310.10(D) | Location change. | None | Restructuring.
310.9 | Corrosive conditions | 310.10(F) | Location change. | None | Restructuring.
310.10 | Temperature limitations of conductors | 310.14(A)(3) | Location change. | None | Restructuring.
310.11 | Marking | 310.8 | Location change. | None | Restructuring.
310.12(A) | Conductor identification | 310.6(A) | Location change. | None | Restructuring.
310.12(B) | Equipment grounding conductor | 310.6(B) | Location change. | None | Restructuring.
310.12(C) | ungrounded conductors | 310.6(C) | Location change. | None | Restructuring.
310.13 | Conductor construction | 310.4 | Location change. | None | Restructuring.
Table 310.13(D) | Thickness of insulation for shielded cables | Table 315.10(B) | Location change. | None | Restructuring.
Table 310.13(E) | Thickness of insulation for shielded cables | Table 315.10(C) | Location change. | None | Restructuring.
310.14 | Aluminum conductors |  | Removed.
310.15(A)(1) | Ampacities - Tables for conductor rating 0-2000V | 310.14(A)(1) | Location change. | None | Restructuring.
310.15(A)(2) | Ampacities - Selection of ampacity | 310.14(A)(2) | Location change. | None | Restructuring.
310.15(B) | Tables (of ampacity) | 310.15(A) | Allows for interpolation between sizes | None | Restructuring.
310.15(B)(2)(a) | Adjustment factors - More than 3 current carrying conductors | 310.15(C)(1) | Location change. | Savings | More detailed data will allow more tightly selected conductor insulation.
310.15(B)(2) Exception 5 | Adjustment factors- Type AC and MC cable | 310.15(C)(1) (d)(1) | Restricts AC and MC to that without an overall outer jacket | Cost | Will increase cost in situations with bundled seal-titer cables.
310.15(B)(2)(c) | Conduits exposed to sunlight | 310.15(B)(2) | Changed to roof-top. Reference tables changed. | None | Rewording.
Table 310.15(B)(2)(c) | Ambient Temperature Adjustment | Table 310.15(B)(1)(1) & Table 310.15(B)(1)(2) | Calculations shifted to include more data and ambient conditions | Savings | More detailed data will allow more tightly selected conductor insulation.
310.15(B)(3) | Bare or covered conductors | 310.15(D) | Location change. | None | Restructuring.
310.15(B)(4) | Neutral Conductor | 310.15(E) | Reworded slightly, but requirements are the same. | None | Restructuring.
310.15(B)(5) | Grounding or bonding conductor | 310.15(F) | Location change. | None | Restructuring.
310.15(C) | Engineering Supervision | 310.14(B) | Simplified calculation by removing dielectric loss temperature rise | None | Insignificant cost impact.
Table 310.13(B) | Thickness of insulation for non-shielded cables | Table 315.10(B) | Location change. | None | Restructuring.
Table 310.13(C) | Conductor application and insulation for conductors rated more than 2001V. | Table 315.10(A) | Location change. | None | Restructuring.
Table 310.13(E) | Thickness of insulation for shielded cables | Table 315.10(C) | Location change. | None | Restructuring.
Table 310.13(E) Note 1 | 100 Percent insulation | 315.10(C)(1) | Location change. Moved to separate paragraph to emphasize. | None | Restructuring.
Table 310.13(E) Note 2 | 133 Percent insulation | 315.10(C)(2) | Location change. Moved to separate paragraph to emphasize. | None | Restructuring.
Table 310.13(E) Note 3 | 173 Percent insulation | 315.10(C)(3) | Location change. Moved to separate paragraph to emphasize. | None | Restructuring.
Table 310.16 & 310.17 | Ampacity Tables - Correction Factors | Table 310.15(B)(1)(1) | Correction factor information moved to separate table. | Savings | New table expands information for lower temperatures, reducing requirements in some cases, but increases some correction factors at higher temperatures.
Table 310.18 & 310.19 | Ampacity Tables - Correction Factors | Table 310.15(B)(1)(2) | Correction factor information moved to separate table. | Savings | New table expands information for lower temperatures, reducing requirements in some cases, but increases some correction factors at higher temperatures.
Table 310.16 | Ampacity Tables | Table 310.16 | Revised down rating of TW & UF to !5A for #14 and 20A for #12 | Cost | Will increase small branch circuit conductor cost.
310.15(B)(6) | Single-Phase dwelling services and feeder reduced size allowance Table 310.12(A) | 310.12(A) & (B) | Location change. | None | Restructuring.
310.15(B)(6) | Single-Phase dwelling services can reduce grounded conductor size to less than phase conductors. | 310.12(D) | Location change. | None | Restructuring.
Figure 310.60 | Cable installation dimensions for use with Table | Figure 315.60(D)(3) | Location change. | None | Restructuring.
310.60(A) | Definitions: Electrical ducts and Thermal resistivity. |  | Removed | None | Covered under other definitions in NEC.
310.60(B) | Ampacities of Conductors Rated 2001 to 35,000V | 315.60(A)(1) | Location change. | None | Restructuring.
310.60(B)(1) | Selection of ampacity | 315.60(A)(2) | Location change. | None | Restructuring.
310.60(C) | Tables use of | 315.60(C) | Location change. | None | Restructuring.
310.60(C)(1) | Grounded Shields | 315.60(D)(1) | Location change. | None | Restructuring.
310.60(C)(2) | Burial depth | 315.60(D)(2) | Location change. | None | Restructuring.
310.60(C)(4) | Ambient not in table calculation | 315.60(D)(4) | Simplified calculation by removing dielectric loss temperature rise | None | Insignificant cost impact.
310.60(D) | Engineering supervision calculation | 315.60(B) | Location change. | None | Restructuring.
310.60(C)(4) |  | 310.15(B)(1) | Simplified calculation by removing dielectric loss temperature rise | None | Insignificant cost impact.
Tables 310.67 - 310.86 | MV Ampacity tables | Tables 315.60(C)(1) - 315.60(C)(20) | Location change. | None | Restructuring.
|  | Table 315.60(D)(4) | Table added for adjustments due to ambient temperatures as alternate to calculations | Savings | Reduced calculation time option.
|  | 315.32(A)(6) | Added requirement for MV cable in corrosive conditions required to be suitable for application. | None | Clarification of requirements already in NEC.
312.1 | Scope - Cabinets and enclosures | 312.1 | Added statement that chapter does not apply to equipment operating over 1000V.
|  | 312.5(C) Exception 2 | Exception added for bushed conduit or tubing associated with a cable tray | Savings | Reduced requirement for box.
|  | Table 312.6(A) | Added Note 2 - Allows use of column for compact AL conductors | Savings | Recognizes use of AL conductors.
312.8 | Enclosures for switches or overcurrent devices - Use as junction or pull box | 312.8(A)(3) | New restriction added for conductors 4 AWG and larger to meet requirements of Table 314.28(A)(2) | Cost | More restrictive on sizing for conductors 4 AWG and larger.
312.8 | Enclosures for switches or overcurrent devices - Use as junction or pull box | 312.8(A)(4) | Add requirement to add a warning label | Cost | Cost of label and installation
|  | 312.8(B) | Add section on power monitoring or energy management equipment allowed in wiring space | Savings | Allows monitoring or metering devices to be installed in wiring space and not in separate enclosures.
|  | 312.10 | Added requirements for screws and fasteners entering cabinets | None | Requirement is broad enough that hardware and installation costs not impacted.
312.10 | Cabinet material | 312.100 | Location change. | None | Restructuring.
312.11 | Spacing | 312.101 | Location change. | None | Restructuring.
|  | 312.102 | Doors or Covers - Added requirement for enclosures to have doors or covers. | None | Enclosure already required in NEC. Clarification
314.5 | Short-Radius conduit bodies | 314.16(C)(3) | Location change. | None | Restructuring.
|  | 314.5 | Screws or Other Fasteners - Added requirements for fasteners | None | Requirement is broad enough that hardware and installation costs not impacted.
314.15 | Damp and wet locations | 314.15 | Added clarifications on allowed installations | None | Clarifications.
314.16 | Number of conductors in device boxes | 314.16 | Clarifications added on intent. | None | Clarifications.
314.16(A) | Box volume calculations | 314.16(A) | Add requirement for barriers | Cost | Restricts number of conductors where boxes have barriers.
314.16(B) | Box fill calculations | 314.16(B) | Adds same requirement as 314.16(A) | Cost | Restricts number of conductors where boxes have barriers.
314.16(B)(5) | Equipment grounding conductor allowance | 314.16(B)(5) | Adds further allowance requirements for grounding conductors over 4 entering a box. | Cost | May increase box sizes.
|  | 314.16(B)(6) | Adds further allowance requirements for terminal blocks in boxes | Cost | May increase box sizes.
Table 314.16(A) | IEC - In the line for 4 × 1 1/4 inch round/octagonal boxes and in the column for 8AWG conductor, delete "5" and insert "4" | Table 314.16(A) | Change made in NEC | None | 2009 IEC Amendment
314.17(B) | Metal boxes and conduit bodies | 314.17(B)(1) | Section changed to cover boxes metal and nonmetallic, with other requirements redistributed. | None | Restructuring.
314.17(C) | Metal boxes and conduit bodies | 314.17(B)(2) | Part of change in box requirement layout. Remove references to UF cable, but covered under "Nonmetallic-sheathed cable". | None | Restructuring.
|  | 314.17(B)(3) | Added section on conductors entering through raceways. | Savings | Clarifies that additional cable or conductor support is not required.
314.23(B)(1) | Nails and screws | 314.23(B)(1) | Added allowances for side mounting holes | Savings | Provides more mounting options
314.23(B)(1) | Nails and screws | 314.23(B)(1) | Added requirement that field installed mounting holes be approved. | Cost | Additional review and approval requirements.
314.23(E) Exception | Raceway support of enclosures | 314.23(E) Exception | Exception adds Type PVC and RTRC | Savings | Allows more flexibility in selection of conduit.
314.24 | Outlet box depth | 314.24 | Changed from depth and adequate clearances to approved dimensions | None | Already required in Section 314.16
314.24(C) | Utilization equipment | 314.24(B) | Location change. | None | Restructuring.
314.24(C)(2) | Conductors larger than #4 AWG | 314.24(B)(2) Exception | Added exception for equipment mounted in junction or pull boxes larger than n100 in2 | Savings | Allows for installation in boxes not listed specifically for purpose.
314.24(C)(4) | Conductors #12 and #10 AWG | 314.24(B)(4) | Adds increased depth requirements for conductors entering center portion of rear of box. | Cost | May require deeper boxes.
|  | 314.24(C) | Added section for requirements for side wiring entrances | Cost | Adds restrictions on sizing boxes.
314.25(B) | Exposed combustible wall or ceiling finish | 314.25(B) | Adds reference to Section 410.23. | Savings | Allows for less than complete covering.
314.27 | Outlet Boxes | 314.27(A) | Location change. | None | Restructuring.
314.27(D) | Boxes at Ceiling-Suspended Fan | 314.27(C) | Added requirements for boxes for future fans. | None | Boxes would still have needed to meet the requirements when fan was installed.
|  | 314.27(E) | Added section for weight supporting receptacles (WSCR) | Savings | Allows for new installation method.
314.28(A)(3) | Smaller Dimensions | 314.28(A)(3) | Adds clarification that where combinations of conductors are allowed by the manufacturer that the mixture of conductors must be part of label as well as number | None | Does not change that conduit bodies need to be applied per the manufacturer's markings.
|  | 314.28(E) | Added section to allow power distribution blocks within pull boxes. | Savings | Allows for wiring method not previously allowed.
314.29 | Boxes Accessibility | 314.29(A) | Added section to clarify requirements inside buildings: Boxes and conduit bodies that are recessed into or behind finished surfaces of buildings shall have access to their internal contents maintained by openings in their covers and in the building finish that comply with 314.29(A)(1), (A)(2), or (A)(3) as applicable. Removable finished covers and faceplates that maintain this access shall be permitted. (1) Boxes 1650 cm3 (100 in.3) or Less in Size. The openings in the building surfaces, if reduced from the outer walls of the box, shall be centered not more than 25 mm (1 in.) from the centerline of the box, and shall not extend beyond the walls of the box. If rectangular, the opening shall be not less than 73 mm (2 7/8 in.) by 45 mm (1 3/4 in.) in size. If circular, the opening shall not be less than 90 mm (3½ in.) in diameter. | None | Clarification
314.29 | Boxes Accessibility | 314.29(A) | Added section to clarify requirements inside buildings: (2) Boxes Larger Than 1650 cm3 (100 in.3) in Size. The openings shall not be smaller than the outer walls of the box. (3) Conduit Bodies. The openings shall not be smaller than outer walls of the conduit body. (B) Underground. Underground boxes and handhole enclosures shall be installed …. | None | Clarification
314.29 | Boxes Accessibility | 314.29(A) Exception | Added Exception: Exception: Smaller openings in building surfaces that accommodate one or more individual devices shall be permitted if all of the following conditions are met: (1) The outlet box that supplies the device(s) is nonmetallic. (2) The branch circuit wiring that supplies each device consists of a separate nonmetallic cable assembly originating outside the box, or individual sets of conductors in a single nonmetallic raceway, all of which originate outside the box. Other than the connections to a single device, these conductors are not spliced in the box or continued to another device, and no other wiring or raceways enter the box. (3) Each device is capable of removal from the building surface opening without being damaged. If a special tool is required for this purpose, the applicable circuit directory for the device records the location of the tool, together with a product code/QR code for acquiring a replacement if necessary. (4) All connections for each device to the branch circuit wiring are made with listed clamping-type wire connectors, which are supplied with the devices. The branch-circuit conductors are arranged to permit the connector(s) to be exposed after the device has been fully removed. (5) The device assemblies are listed for this application. | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
314.29 | Boxes Accessibility | 314.29(B) Exception | Added to exception that location description of covered handholes must available to authorized personnel | None | Clarification on requirements for "effectively identified"
314.30(A) | Handhole Enclosures - Sizes | 314.30(A) | Changed from conductors operating at over 600V to conductors operating over 1000V | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
314.70 | Pull and Junction Boxes over 600V | 314.70 | Changed from 600V to 1000V | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
|  | 314.70(B) | Conduit Bodies - Added | None | Clarification on requirements.
|  | 314.70(C) | Handhole Enclosures - Added | None | Clarification on requirements.
314.71 | Size of Pull and Junction Boxes | 314.71 | Added conduit bodies if they meet requirements. | Savings | Allows for new installation method.
314.71 Exception\ | Size of Pull and Junction Boxes | 314.71 | Exception removed for terminal housing supplied with motors. | None | Motor terminal housing requirements already in NEC under Section 430.
|  | 314.102 | Bushings - Added | None | Conductor protection, along with requirements on bushings, already in NEC
|  | 320.6 | Added - AC Cable and fittings shall be listed. | Cost | Requirement that AC cable and fittings will increase material cost due to testing requirements.
|  | 322.6 | Added - FC Cable and fittings shall be listed. | Cost | Requirement that FC cable and fittings will increase material cost due to testing requirements.
322.2 | Definition of FC cable |  | Definition removed for FC | None | Uses is defined in later parts of the section which cover definition.
322.12(3) | Uses not permitted | 322.12(3) | Allows for uses were permitted in this Code | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
324.2 | Definition of FC cable |  | Definition removed for FCC | None | Uses is defined in later parts of the section which cover definition.
324.12(4) | Not Permitted - School or Hospital | 324.12(5) | Reduced restriction by allowing in office areas | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
324.41 | Floor covering | 324.41 | Size of carpet square \s increased to 1 meter which will reduce labor costs | Savings | Reduced carpet installation labor is possible.
362.2 | Definition of FC cable |  | Definition removed for IGS | None | Uses is defined in later parts of the section which cover definition.
328 | Medium Voltage Cable (MV) | 315 | MV cable relocated and expanded to new chapter. | None | Restructuring.
|  | 315.1 | Added - Inclusion of fittings and terminations.
|  | 315.6 | Added - MV Cable and fittings shall be listed Starting 1/2026 | Cost | Requirement that MV cable and fittings will increase material cost due to testing requirements.
|  | 315.10 | Added - Construction | None | Restructuring.
|  | 315.12 | Added - Minimum size of conductors | None | Already covered under Tables 315.60(C)(3) - 315.60(C)(@)
310.4 | Stranded conductors | 315.12(C) | Clarification of application to MV cables | None | Restructuring.
310.11 | Marking | 315.14 | Conductor identification | None | Restructuring.
310.11 | Marking | 315.16 | Marking | None | Restructuring.
|  | 315.17 | Added - Marking MV joints and terminations | Cost | Added requirement for marking.
|  | 315.30 | Added - Installation by qualified person(S) | Cost | Adds higher level of training and documentation
|  | 315.32(A)(6) | Added - Installation in corrosive conditions where suitable | Savings | Allows more flexibility for wiring methods for systems from 2000V to 35,000V.
328.10 | MV Uses permitted | 315.32(A) | Order of uses changed, but same scope. | None | Restructuring.
328.12 | Uses not permitted - exposed to direct sunlight | 315.32(A)(8) | Added - allows use in direct sunlight where identified for use | Savings | Allows more flexibility for wiring methods for systems from 2000V to 35,000V.
|  | 315.32(B) | Added - Requirements for joints and terminations | Cost | Adds requirements for joints and terminatio0ns.
|  | 315.45 | Added - Requirements for shielding at joints and terminations | Cost | Adds requirements for joints and terminatio0ns.
330.2 | Definition of MC cable |  | Definition removed for MC | None | Uses is defined in later parts of the section which cover definition.
330.40 | Boxes and fittings listing | 330.6 | Location change. | None | Restructuring.
330.10 | Uses permitted - MC cable | 330.10(A)(11)c. | Removed need for corrosion resistant jacket where insulated conductors under the armor are listed for wet locations | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
|  | 330.15 | Added - Exposed work | None | Requirements contained under 300
330.30(B) | Securing - MC cable | 330.30(B) | Added - Requirement for supporting in vertical installations not exceeding 10-feet | Savings | Removes prior requirement for support every 6-ffet.
|  | 330.30(D)(3) | Added option to use to connect to equipment where flexibility is required up to 3-feet | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
310.15(B)(2)(a) | Adjustment factors - More than 3 current carrying conductors | 330.80(C) | Clarification of requirement applying to MC cable | None | Requirement already under 310.15
|  | 330.130 | Added - Type MC-HL for use in hazardous (Classified) locations | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
332.2 | Definition of MI cable |  | Definition removed for MI | None | Uses is defined in later parts of the section which cover definition.
322.40 | Boxes and fittings identified for use | 332.6 | Added - MI Cable and fittings shall be listed. | None | Restructuring.
334 | NM, NMC & NMS cable | 334 | Removed NMS cable from article
334.2 | Definition of NM, NMC & NMS cable |  | Definition removed for NM, NMC & NMS | None | Uses is defined in later parts of the section which cover definition.
334.10(2) | IEC - In any building or structure not exceeding three stories (see Section 362.10 for the definition of STORY) | 334.10(2) |  |  | 2009 IEC Amendment
334.10(2)(a) | IEC - For exposed work except as prohibited in Section 334.12. | 334.10(2)(a) |  |  | 2009 IEC Amendment
334.10(2)(b) | IEC - Concealed within walls, floors, and ceilings except as prohibited in Section 334.12. | 334.10(2)(b) |  |  | 2009 IEC Amendment
334.10(3) | IEC - In any building or structure exceeding three stories (see Section 362.10 for the definition of STORY), Type NM, Type NMC, and Type NMS cables shall be concealed within walls, floors, and ceilings that provide a thermal barrier of material that has at least a 15-minute finish rating identified in listings of fire-rated assemblies. The 15-minute-finish-rated thermal barrier shall be permitted to be used for combustible walls, floors, and ceilings, except as prohibited in Section 334.12. | 334.10(3) |  |  | 2009 IEC Amendment
334.10(3) Exception | IEC - Exception: Where the building is provided with an approved automatic sprinkler system throughout, Type NM, Type NMC, and Type NMS cables are permitted to be used within walls, floors, ceilings, exposed or concealed, in buildings exceeding three stories. | 334.10(3) Exception |  |  | 2009 IEC Amendment
334.10(1) | Uses permitted for NM, NMC | 334.10(1) | Added - Attached and detached garages and storage buildings single family | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
334.10(2) | Uses permitted for NM, NMC | 334.10(2) | Added - Attached and detached garages for multi-family | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
334.12(A) Exception | Permitted to be installed in Types I and II in raceways | 334.10(5) | Added - permitted to be installed in Types I and II in raceways | None | Allows more flexibility for wiring methods for systems from 600V to 1000V.
334.15(B) | Protected from physical damage | 334.15(B) | Added - Conduit to be protected on ends with bushings. | None | Required on conduit sleeves.
|  | 334.19 | Added - Cable Entries sheath removal | None | Installation without cost impact
334.24 | Bending Radius - NM | 334.24 | Added - for flat cables maximum dimension to be used for cable bending radius | None | Installation without cost impact
|  | 335 | Instrumentation Tray Cable - Type ITC | Savings | New cable type recognized by the NEC. Allows more flexibility for wiring methods for systems from 600V to 1000V.
336.2 | Definition of FC cable |  | Definition removed for TC | None | Uses is defined in later parts of the section which cover definition.
|  | 336.6 | Added - TC Cable and fittings shall be listed. | Cost | Requirement that TC cable and fittings be listed will increase material cost due to testing requirements.
|  | 336.10(9) | Added - For one and two family dwellings Type TC-ER-JP permitted for branch circuits | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
|  | 336.10(10) | Added - Direct buried where identified for use | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
|  | 336.10(11) | Added - In hazardous locations were specifically permitted | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
|  | 336.10(12) | Added - For service entrance where identified for such use TC-ER | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
|  | 336.130 | Added - Type TC-ER-HL for use in hazardous (Classified) locations | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
|  | 337 | Added Type P cable | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
338 | Definition of SE & USE cable |  | Definition removed for MC | None | Uses is defined in later parts of the section which cover definition.
|  | 338.6 | Added - Listing of SE & USE Cables |  | Requirement that SE & USE cable and fittings be listed will increase material cost due to testing requirements.
338.10(B)(4)(a) | Uses Permitted - Interior | 338(B)(4)(a) | Expanded to cover requirements explicitly. | None | Clarification of requirements previously referenced.
338.10(B)(4)(b) | Uses Permitted - Exterior | 338(B)(4)(b) | Expanded to cover requirements explicitly. | None | Clarification of requirements previously referenced.
338.24 | Bending Radius - SE & USE | 338.24 | Added - major diameter to be used for cable bending radius | None | Installation without cost impact
340.2 | Definition of UC cable |  | Definition removed for UF | None | Uses is defined in later parts of the section which cover definition.
|  | 340.10(5) | Added - PV Uses | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
340.24 | Bending Radius - UF | 340.24 | Added - for flat cables maximum dimension to be used for cable bending radius | None | Installation without cost impact
342.2 | Definition of IMC |  | Definition removed for IMC | None | Uses is defined in later parts of the section which cover definition.
|  | 342.10(E) | Added - Approved for locations subject to sever physical damage | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
342.14 | Dissimilar Metals | 342.14 | Added - Stainless steel and aluminum fittings permitted to be used with galvanized IMC in non-corrosive installations | Savings | Allows more flexibility in selection of raceways.
|  | 342.14 | Added - Stainless steel IMC to be used only with stainless steel boxes and fittings. | Cost | Adds restrictions on application of stainless steel IMC.
342.20(B) | Maximum size for IMC | 342.20(B) | Maximum size increased to 6" | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
342.30(C) | Unsupported IMC |  | Article removed, but 18" nipples covered under other sections. | None | Requirements covered in other sections.
|  | 342.100 | Added - Construction | Cost | Requirements for IMC.
342.130 | Standard Lengths - IMC |  | Deleted | None | No cost impact to standard lengths.
344.2 | Definition RMC | 344.100 | Construction | None | Restructuring.
|  | 342.10(E) | Added - Approved for locations subject to sever physical damage | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
344.14 | Dissimilar Metals | 344.14 | Added - Stainless steel and aluminum fittings permitted to be used with galvanized RMC in non-corrosive installations | Savings | Allows more flexibility in selection of raceways.
|  | 344.14 | Added - Stainless steel RMC to be used only with stainless steel boxes and fittings. | Cost | Adds restrictions on application of stainless steel RMC.
|  | 344.28 | Reaming and Threading - Added requirements for PVC coated RMC. | None | Requirement to meet manufacturer's requirements.
344.30(C) | Unsupported IMC |  | Article removed, but 18" nipples covered under other sections. | None | Requirements covered in other sections.
344.130 | Standard Lengths - IMC |  | Deleted | None | No cost impact to standard lengths.
348.2 | Definition of FMC |  | Definition removed for FMC | None | Uses is defined in later parts of the section which cover definition.
|  | 348.2 | Reconditioned - Prohibited | Cost | Prohibits reconditioning.
350.2 | Definition of LFMC |  | Definition removed for LFMC | None | Uses is defined in later parts of the section which cover definition.
|  | 350.2 | Reconditioned - Prohibited | Cost | Prohibits reconditioning.
350.12(2) | Uses Not Permitted - LFMC | 350.10(4) | Changed wording to permitted with same requirement | None | Restructuring.
352.2 | Definition of PVC |  | Definition removed for PVC | None | Uses is defined in later parts of the section which cover definition.
352.10 | Uses Permitted -PVC | 352.10(B) | Added - Concrete encased. | Savings | Allows more flexibility in selection of raceways.
352.12(C) | Uses Not Permitted - PVC subject to physical damage | 350.10(K) | Changed wording to permitted with same requirement | None | Restructuring.
352.12(E) | Uses Not Permitted - PVC Conductors of higher temperature | 350.10(J) | Changed wording to permitted with same requirement | None | Restructuring.
352.30(C) | Unsupported PVC |  | Article removed, but 18" nipples covered under other sections. | None | Requirements covered in other sections.
352.44 | Expansion Fittings - PVC | 352.44(B) | Added - Requirement for underground conduit emerging from the ground for frost heave or other movement. | Cost | Requires addition of expansion fittings.
353.2 | Definition of HDPE |  | Definition removed for HDPE | None | Uses is defined in later parts of the section which cover definition.
353.12(E5 | Uses Not Permitted - HDPE Conductors of higher temperature | 350.10(6) | Changed wording to permitted with same requirement | None | Restructuring.
354.2 | Definition of NUCC |  | Definition removed for NUCC | None | Uses is defined in later parts of the section which cover definition.
354.60 | Grounding - NUCC | 354.60 Exception 1 | Added - Exception for running separately per 250.134 Exception 2 | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
354.60 | Grounding - NUCC | 354.60 Exception 2 | Added - Exception for not requiring grounding conductor per 250.142 | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
355.2 | Definition of RTRC |  | Definition removed for RTRC | None | Uses is defined in later parts of the section which cover definition.
355.12(E) | Uses Not Permitted - RTRC Conductors of higher temperature | 355.10(I) | Changed wording to permitted with same requirement | None | Restructuring.
355.30(C) | Unsupported RTRC |  | Article removed, but 18" nipples covered under other sections. | None | Requirements covered in other sections.
356.2 | Definition of LFNC |  | Definition removed for LFNC | None | Uses is defined in later parts of the section which cover definition.
356.10(5) | Type LFNC-B lengths longer than 6-feet | 356.10(5) | Removed specific reference to LFNC-B | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
|  | 356.10(8) | Added - Permitted in locations subject to sever corrosion | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
|  | 356.90(9) | Added - Permitted to use conductors with higher temperature rating if rating is limited to LFNC | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
356.12(4) | Not Permitted - Operating voltage of conductors exceeds 600V |  | Deleted | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
356.30 | Securing and Supporting - LFNC-B | 356.30 | Removed specific reference to LFNC-B | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
358.2 | Definition of EMT |  | Definition removed for EMT | None | Uses is defined in later parts of the section which cover definition.
358.10 | Uses Permitted - EMT | 356.10(3) | Added - Permitted in hazardous locations | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
358.10 | Uses Permitted - EMT | 356.10(4) | Added - Permitted manufactured wiring systems | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
|  | 356.10(B)(2) | Added - Requirements for corrosion protection for AL EMT | Cost | Additional requirements.
|  | 356.10(C) | Permitted EMT installed in Cinder fill | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
|  | 356.10(E) | Permitted EMT in locations subject to physical damage | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
|  | 356.14 | Added - Stainless steel EMT to be used only with stainless steel boxes and fittings. | Cost | Adds restrictions on application of stainless steel RMC.
358.20(B) | Maximum size for EMT | 358.20(B) | Maximum size increased to 6" | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
358.30(C) | Unsupported EMT |  | Article removed, but 18" nipples covered under other sections. | None | Requirements covered in other sections.
360.2 | Definition of FMT |  | Definition removed for FMT | None | Uses is defined in later parts of the section which cover definition.
360.40 | Boxes and Fittings - FMT require effectively closed openings |  | Deleted | None | Requirement for closed boxes and openings elsewhere in NEC.
362.2 | Definition of ENT |  | Definition removed for ENT | None | Uses is defined in later parts of the section which cover definition.
|  | 362.2 | Reconditioned - Prohibited | Cost | Prohibits reconditioning.
362.10 | IEC - For the purpose of this section, a story is that portion of a building included between the upper surface of any floor and the upper surface of the floor next above, except that the topmost story shall be that portion of a building included between the upper surface of the topmost floor and the ceiling or roof above. If the finished floor level directly above a usable or unused under-floor space is more than 6 feet above grade for more than 50 percent of the total perimeter or is more than 12 feet above grade at any point, such usable or unused under-floor space shall be considered as a story. The use of ENT and fittings shall be permitted in the following | 362.10 |  |  | 2009 IEC Amendment
362.10(1) | IEC - In any building exceeding three stories as follows: | 362.10(1) | Change of "floors abvoe grade" to "stories" |  | 2009 IEC Amendment
362.10(2) | IEC - In any building exceeding three stories. ENT shall be concealed... | 362.10(2) | Change of "floors abvoe grade" to "stories" |  | 2009 IEC Amendment
362.10(2) | IEC - Add: Where the building is provided with an approved automatic sprinkler system throughout, ENT is permitted to be used within walls, floors, and ceilings, exposed, concealed, in buildings exceeding three stories. | 362.10(2) Exception 2 | Moved exception for buildings protected by sprinkler to body of 362.10(2) | None | 2009 IEC Amendment
362.10(5) | IEC - Add: Where the building is provided with an approved automatic sprinkler system throughout, ENT is permitted to be used within walls, floors, and ceilings, exposed, concealed, in buildings exceeding three stories. | 362.10(5) Exception 5 | Moved exception for buildings protected by sprinkler to body of 362.10(5) | None | 2009 IEC Amendment
362.12(4) | Uses Not Permitted - ENT higher conductor temperature rating | 362.10(10) | Changed wording to permitted with same requirement | None | Restructuring.
362.12(6) | Uses Not Permitted - ENT for voltages over 600V |  | Deleted | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
362.12(7) | IEC - Add: 362.10(2) | 362.12(5) |  |  | 2009 IEC Amendment
362.20(B) | Maximum size for ENT | 362.20(B) | Maximum size increased to 2-1/2" | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
362.60 | Grounding - ENT | 362.60 Exception 1 | Added - Exception for running separately per 250.134 Exception 2 | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
362.60 | Grounding - ENT | 362.60 Exception 2 | Added - Exception for not requiring grounding conductor per 250.142 | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
366.2 | Definition of Auxiliary Gutters |  | Definition removed for Auxiliary Gutters | None | Uses is defined in later parts of the section which cover definition.
366.12(2) | Uses Not Permitted - Auxiliary Gutters | 366.10(C) | Added - Auxiliary Gutters extended up to 30-feet | None | Restructuring.
|  | 366.20 | Added - Conductors installed in parallel | None | Clarification of requirements already in the NEC
366.22(A) | Metal Auxiliary Gutters derating |  | Deleted | None | Clarification of requirements under 366.23(A)
368.2 | Definition of Busways |  | Definition removed for Busways | None | Uses is defined in later parts of the section which cover definition.
368.17(C) | Feeder or Branch Circuit Overcurrent - Busway Taps | 368.17(C) Exception 4 | Added - Allows for bus plugs to be non-accessible from floor where a readily accessible disconnect is supplied | Savings | Allows more flexibility in selection of raceway and potential labor and material cost savings.
368 Part IV | Requirements for Busway over 600V | 368 Part IV | Changed to over 1000V | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
|  | 369 | Added Section - Insulated Bus Pipe (IBP) | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
370 | Cablebus |  | Section reorganized | None | Restructuring.
370.2 | Definition of Cablebus |  | Definition removed for Cablebus | None | Uses is defined in later parts of the section which cover definition.
|  | 371 | Added Section - Flexible Bus Systems | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
372 | Cellular Concrete Floor Raceways |  | Section reorganized | None | Restructuring.
372.2 | Definition of Cellular Concrete Floor Raceways |  | Definition removed for Cellular Concrete Floor Raceways | None | Uses is defined in later parts of the section which cover definition.
374 | Cellular Metal Floor Raceways |  | Section reorganized | None | Restructuring.
374.2 | Definition of Cellular Metal Floor Raceways |  | Definition removed for Cellular Metal Floor Raceways | None | Uses is defined in later parts of the section which cover definition.
|  | 374.6 | Added - Listing of Cellular Metal Floor Raceways | Cost | Adds requirement for listing of material.
376.2 | Definition Metal Wireways |  | Definition removed for Metal Wireways | None | Uses is defined in later parts of the section which cover definition.
376.10(2) | Uses Permitted - Metal Wireways in concealed locations | 376.10(2) | Removed and only allowed for extensions through walls | Cost | Restricts uses.
376.10(3) | Uses Permitted - Metal Wireways in hazardous locations includes wet locations | 376.10(2) | Moved to separate paragraph | None | Restructuring.
|  | 376.20 | Added - Conductors installed in parallel | None | Clarification of requirements already in the NEC
376.56(B)(1) | Installation - Power Distribution Blocks | 376.56(B)(1) | Added - If used on line side of service equipment must be marked as suitable | None | Required under other sections of the NEC
|  | 376.56(B)(5) | Added - Conductors shall be arranged so that power distribution blocks remain unobstructed. | Cost | Restriction on installation.
|  | 376.60 | Added - Grounding for use of listed metal wireways as grounding conductor | Savings | Reduces cost by removing need for separate grounding conductor.
378.2 | Definition Nonmetallic Wireways |  | Definition removed for Nonmetallic Wireways | None | Uses is defined in later parts of the section which cover definition.
|  | 378.20 | Added - Conductors installed in parallel | None | Clarification of requirements already in the NEC
|  | 380.12(7) | Added - Uses Not Permitted for Multioutlet Assemblies where cord and plug connected. | Cost | Restricts use of material.
|  | 380.23 | Added - Insulated Conductors | None | Reflects requirements elsewhere in the NEC
|  | 380.23(A) | Added - Deflected conductors | None | Reflects requirements elsewhere in the NEC
|  | 380.23(B) | Added - Multioutlet Assemblies used as pull boxes | None | Reflects requirements elsewhere in the NEC
382.2 | Definition Nonmetallic Extensions |  | Definition removed for Nonmetallic Extensions | None | Uses is defined in later parts of the section which cover definition.
384.2 | Definition Strut-Type Channel Raceway |  | Definition removed for Strut-Type Channel Raceway | None | Uses is defined in later parts of the section which cover definition.
|  | 384.10(4) | Deleted - Permitted for 600V or less | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
384.22 | Number of conductors in Strut-Type Channel Raceway - Equation |  | Equation deleted, but requirements still the same | None
386.2 | Definition Surface Metal Raceway |  | Definition removed for Surface Metal Raceway | None | Uses is defined in later parts of the section which cover definition.
|  | 386.120 | Added - Marking of each length of surface metal Raceway | Cost | Added cost of marking
388.2 | Definition Surface Nonmetallic Raceway |  | Definition removed for Surface Nonmetallic Raceway | None | Uses is defined in later parts of the section which cover definition.
|  | 388.120 | Added - Marking of each length of surface nonmetallic Raceway | Cost | Added cost of marking
392.2 | Definition Cable Trays |  | Definition removed for Cable Trays | None | Uses is defined in later parts of the section which cover definition.
392.3 | Uses Permitted - Cable Trays | 392.10 | Added - Cables and single insulated conductors to be installed per 392.10(B)(1) | None | Clarification of requirement already in article 392.
Table 392.3(A) | Wiring Methods for allowed for Cable Tray | Table 392.10(A) | Removed - Optical Fiber Raceways | Cost | Reduces wiring options.
Table 392.3(A) | Wiring Methods for allowed for Cable Tray | Table 392.10(A) | Removed - Signaling Raceways | Cost | Reduces wiring options.
392.3(C) | Cable Trays can be used as equipment grounding conductor where continuous maintenance and supervision apply | 392.60 | Location change. | None | Restructuring.
|  | 392.10(E) | Added - Airfield lighting MV circuits can be installed in cable tray where maintained by qualified personnel | Savings | Allows more flexibility for wiring methods for MV systems.
392.5 | Construction Specifications for Cable Tray | 392.100 | Location change. | None | Restructuring.
392.6 | Installation - Cable Tray | 392.18(B) | Added - Cable tray section must be complete before cable installation. | Cost | Restriction on installation and prohibits shop fabrication.
392.6 | Installation - Requirement not to exceed 6-feet between cable tray and other raceways or equipment cabinets. | 392.30(B)(3) | Location change. | None | Restructuring.
392.6(C) | Installation - Prevention of stress on cables | 392.30(B)(2) | Location change. | None | Restructuring.
392.6(E) | Installation - Multiconductor cables under 600V | 392.20(A) | Changed - Multiconductor cables under 1000V | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
382.6(F) | Installation - Cables over 600V | 392.20(B) | Changed - Cables over 1000V | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
392.7(A) | Grounding - Cable Trays | 392.60(A) | Location change. | None | Restructuring.
392.7(B) | Grounding - Steel or AL Cable Trays | 392.60(B) | Location change. | None | Restructuring.
392.8(A) | Cable Installation - Cable splices in Cable Tray | 392.56 | Location change for MV only | None | Restructuring.
392.8(B) | Cable Installation - Fastened securely in Cable Tray | 392.30(B)(1) | Location change. | None | Restructuring.
392.8(C) | Cable Installation - Bushed conduit and tubing | 392.46(B) | Location change. | None | Restructuring.
392.8(D) | Cable Installation - Connected in parallel | 392.20(C) | Location change. | None | Restructuring.
392.8(E) | Cable Installation - Single Conductors | 392.20(D) | Location change. | None | Restructuring.
392.9 | Number of Multiconductor cables | 392.22(A) | Added - Fill calculations to be performed separately for each side of a doodad tray | None | Clarification
392.10(A) | Number of single-conductor cables rated 2000V or less in ladder or ventilated tray | 392.22(B) | Location change. | None | Restructuring.
392.11 | Ampacity of Cables rated 200V or less | 392.80(A) | Location change. | None | Restructuring.
392.11(C) | Combinations of single-conductor and multi-conductor | 392.80(A)(3) | Location change. | None | Restructuring.
392.12 | Number of MV cables | 392.22(C) | Location change. | None | Restructuring.
392.13 | Ampacity of MV cables | 392.80(B) | Location change. | None | Restructuring.
|  | 393 | Added Section - Low-Voltage Suspended Ceiling Power Distribution Systems | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
394.2 | Definition of Knob-and-tube |  | Definition removed for Knob-and-tube | None | Uses is defined in later parts of the section which cover definition.
|  | 395 | Added Section - Outdoor Overhead Conductors Over 1000V | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
396.2 | Definition of Messenger-supported Wiring |  | Definition removed for Messenger-supported wiring | None | Uses is defined in later parts of the section which cover definition.
398.2 | Definition of Open wiring on insulators |  | Definition removed for Open wiring on insulators | None | Uses is defined in later parts of the section which cover definition.
398.10 | Uses Permitted - Open Wiring | 398.10 | Changed 600V to 1000V | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.
398.15(C)(4) | Exposed to Physical Damage | 398.15(C)(4) | Added RTRC as acceptable raceway | Savings | Allows more flexibility for wiring methods for systems from 600V to 1000V.