## Response 1
Current 2009 Code | 2023 NEC Code | Summary of Change | Rational for Change | Fiscal Analysis
FPN (Fine Print Note) is now referred to as Informational Note
400.1 |  | No change |  | 0
400.2 |  | No change |  | 0
400.3 |  | No change |  | 0
400.4 | 400.4 | Clarifying text | Makes it clear who has jurisdiction for uses not described in Table 400.4 | 0
NEC Leave in order as it is in 2009
Table 400.4 |  | Text for 400.5 is placed ahead of Table 400.4. Use 2023 NED Table 400.4 | It is easier to read if the code text is placed ahead of the table that it applies to. NEC 2023 Table 400.4 has been updated since 2009 | 0
400.5 |  | New tables | Updated tables | 0
400.6 |  | No change |  | 0
400.7, .8, .9, .10, .11, .12, .13, .14 |  | All re-numbered to 10 through 17 in 2023 | NEC update | 0
400.2 | 400.2 | No change |  | 0
400.21 | 400.21 | Use NEC wording and standard, elimnate exception | Any flexible cord will already meet the NEC standard. | 0
400.22 | 400.22 | Use NEC wording and standard, elimnate exception | No need to reinvent the wheel | 0
400.23 | 400.23 | No change |  | 0
400.24 | 400.24 | No change |  | 0
Part III | Part III | Use NEC wording (up to 2000V) | NEC has added Part IV (over 2000V)
| Part IV | New NEC revision
Article 402
402.3 |  | Do not change location, but use up dated table from NEC | Indiana Table location is better located than 2023 NEC because it is directly after 402.3.
2023 NEC table has been updated.
402.4 | 402.4 | Does not exist in either code
402.5 |  | No change
402.6 |  | No change
402.11 | 402.12 | Renumbered to 402.12 | Match NEC numbering
402.12 | 402.14 | 402.12 renumbered to 402.14 | Match NEC numbering
404
404.1 | 404.1 | Use 2023 NEC text | Updated text | 0
404.2 A&B | 404.2 A&B | No change
| 404.2C | Code revision - Add to Indiana Code | Most dimmer switches now require a neutral. | ~ $100/house
404.3 | 404.3 | No change
404.4 | 404.4 | Revise to NEC text | NEC text is clearer | 0
404.5 | 404.5 | No change
404.6 | 404.6 | Revise to NEC text | Additionat text in NEC | 0
404.7 | 404.7 | No change
404.8 | 404.8 | Revise to NEC text | Additionat text in NEC | 0
404.9 | 404.9 | Revise to NEC text | NEC revised text adds clarity | 0
410.142 | 410.142 | No Change
410.143 | 410.143 | No Change
410.144 | 410.144 | No Change
410.145 | 410.145 | No Change
410.146 | 410.146 | Use NEC text
410.147
Part XIV
410.15 | 410.15 | Use NEC text
410.153 | 410.153 | No Change
410.154 | 410.154 | No Change
410.155 | 410.155 | Use NEC text
Part XV
410.16 | 410.16 | No Change
Part XVI
| 410.170-410.195 | Add to Indiana code | New NEC section
Article | 411 | Use all of NEC text | Updated text

## Response 2
CODE | CHANGE | REASON FOR CHANGE | DOLLAR ATTRIBUTED TO CHANGE
406.12 | Temper proof devices required | Consumer Safety | $350-450.00 per home | (the push was because it requires coordination to intentionally fill two holes at once in the device for you to be able to plug in a load and most toddlers don't have that coordination or intention)
422.18 with reference to 314.27 (E) | Paddle Fan Box Type | Ensure the fan does not fall | $35-40.00 per home | (this is just for extra security of a heavy fan or fixture)
422.5 | GFI's on Dishwasher plug | Consumer Safety | $35-40.00 per home | (standard GFI protection for loads that could come in contact with water)
422.5 | GFI's on sump, sump back up, etc | Consumer Safety | $160.00 per home | (standard GFI protection for loads that could come in contact with water, this could be a nightmare if you have a finished basement and have no back up or alarm tied to it)
495.46 | Breaker Lock | Lock breaker to off mode if someone is working on the circuit | $35-40.00 per home | (this is a carry over from the commercial world…seems excessive)

## Response 3
Line Item | 2009 Section | 2023 Section | Name | Summary Of Change | Fiscal Impact ($/Unit)
18 | 406.11 | 406.12 | Tamper Resistant Receptacles | All 15AMP and 20AMP receptacles in the house must be tamper resistant, except when above the floor by 5.5ft, part of a luminaire or appliance, for an appliance. Also found in 210.52 and 550.13 | 2
25 | 210.8 | 422.5 (A) | GFCI Protection | Section 210.8 provides GFCI requirements for certain receptacles and outelts, whereas this section 422.5 provides GFCI protection requirements for specific appliances. 2017 NEC, only dwelling unit dishwashers required GFCI protection in accordance with 210.8(D). This language was shortened up and relocated to 422.5(A) in the 2020 NEC and now applies to all dishwashers. THIS IS FOR THE DISHWASHER | 39.474
26 | 210.8 | 422.5 (A) | GFCI Protection | Same explanation as above. THIS IS FOR THE SUMP PUMP | 39.474
32 | 422.33 | 422.31 | Disconnection of Permanently Connected Appliances | Disconnection must be "within sight from the appliance” while flipping the switch or while servicing the appliance, the switch can be seen by the electrician and it is within 50 feet. If not, the breaker must be lockable | 0